## README
ALT_CP_Ref_V7_9 equipment register
Purpose | The single file that says which equipment the site has. The builder reads it and generates the station, Field IO, point mapping, 3D and 2D drawings consistently.
Equipment | chiller / CHP / CDP / CT, 6 slots each (01-02 = existing V7.8 units, 03-06 = expansion slots) · Installed = Y/N
Sensors | additional sensors (SNS01...), any number of rows, at least 6 slots · Kind: Temp, RH, Pressure, DP, Flow, Power, Level, Generic
AirSide | floor AHUs 2-8 (floor 1 = AHU01/02, OAU01 of V7.8) · Installed = Y/N
Systems | future systems (fire alarm, fire protection, lighting, power) · one device per row: floor, X/Y/Z position (mm), station point -> shown in 3D with its status
Add equipment (method 1, no rebuild) | In Workbench set <slot>_Installed = true (e.g. CH03_Installed) -> the logic counts the unit at once -> wire the Field IO group <slot> -> P2P test
Add equipment (method 2, rebuild) | Edit this file (Installed = Y, Protocol, Device) -> run make_v79.py --register <this file> -> new config.bog + point register + 3D that match
Remove equipment | Set Installed = N (or <slot>_Installed = false in Workbench) -> the unit is not selected, never started and shown as a ghost in 3D
Protocol | 1 BACnet/IP · 2 BACnet MS/TP · 3 Modbus TCP · 4 Modbus RTU · 5 hard-wired I/O

## Equipment
Slot | Type | Tag | Installed | Description | Rated | Protocol | Device | Address | Notes
CH01 | CH | CH-01 | Y | Chiller 1 | 334 TR | 1 |  |  | base unit (V7.8 logic)
CH02 | CH | CH-02 | Y | Chiller 2 | 334 TR | 1 |  |  | base unit (V7.8 logic)
CH03 | CH | CH-03 | N | Chiller 3 | 334 TR | 1 |  |  | expansion slot
CH04 | CH | CH-04 | N | Chiller 4 | 334 TR | 1 |  |  | expansion slot
CH05 | CH | CH-05 | N | Chiller 5 | 334 TR | 1 |  |  | expansion slot
CH06 | CH | CH-06 | N | Chiller 6 | 334 TR | 1 |  |  | expansion slot
CHP01 | CHP | CHP-01 | Y | Chilled water pump 1 | 800 USgpm / 22 kW | 4 |  |  | base unit (V7.8 logic)
CHP02 | CHP | CHP-02 | Y | Chilled water pump 2 | 800 USgpm / 22 kW | 4 |  |  | base unit (V7.8 logic)
CHP03 | CHP | CHP-03 | N | Chilled water pump 3 | 800 USgpm / 22 kW | 4 |  |  | expansion slot
CHP04 | CHP | CHP-04 | N | Chilled water pump 4 | 800 USgpm / 22 kW | 4 |  |  | expansion slot
CHP05 | CHP | CHP-05 | N | Chilled water pump 5 | 800 USgpm / 22 kW | 4 |  |  | expansion slot
CHP06 | CHP | CHP-06 | N | Chilled water pump 6 | 800 USgpm / 22 kW | 4 |  |  | expansion slot
CDP01 | CDP | CDP-01 | Y | Condenser water pump 1 | 1,000 USgpm / 30 kW | 4 |  |  | base unit (V7.8 logic)
CDP02 | CDP | CDP-02 | Y | Condenser water pump 2 | 1,000 USgpm / 30 kW | 4 |  |  | base unit (V7.8 logic)
CDP03 | CDP | CDP-03 | N | Condenser water pump 3 | 1,000 USgpm / 30 kW | 4 |  |  | expansion slot
CDP04 | CDP | CDP-04 | N | Condenser water pump 4 | 1,000 USgpm / 30 kW | 4 |  |  | expansion slot
CDP05 | CDP | CDP-05 | N | Condenser water pump 5 | 1,000 USgpm / 30 kW | 4 |  |  | expansion slot
CDP06 | CDP | CDP-06 | N | Condenser water pump 6 | 1,000 USgpm / 30 kW | 4 |  |  | expansion slot
CT01 | CT | CT-01 | Y | Cooling tower 1 | 420 TR (1 cell, 5.5 kW fan) | 4 |  |  | base unit (V7.8 logic)
CT02 | CT | CT-02 | Y | Cooling tower 2 | 420 TR (1 cell, 5.5 kW fan) | 4 |  |  | base unit (V7.8 logic)
CT03 | CT | CT-03 | N | Cooling tower 3 | 420 TR (1 cell, 5.5 kW fan) | 4 |  |  | expansion slot
CT04 | CT | CT-04 | N | Cooling tower 4 | 420 TR (1 cell, 5.5 kW fan) | 4 |  |  | expansion slot
CT05 | CT | CT-05 | N | Cooling tower 5 | 420 TR (1 cell, 5.5 kW fan) | 4 |  |  | expansion slot
CT06 | CT | CT-06 | N | Cooling tower 6 | 420 TR (1 cell, 5.5 kW fan) | 4 |  |  | expansion slot

## Sensors
Slot | Installed | Tag | Description | Kind | Unit | ValidLo | ValidHi | AlarmLo | AlarmHi | SimValue | Location | Protocol | Address
SNS01 | N | TT-CHWS-B | CHW supply temp, building branch B | Temp | C | -10 | 60 | 5 | 35 | 24 | Plant room | 5
SNS02 | N | PT-CHW-RISER | CHW riser pressure, top floor | Pressure | kPa | -50 | 1600 | 50 | 900 | 350 | Roof | 5
SNS03 | N | TT-PLANTRM | Plant room air temperature | Temp | C | -10 | 60 | 5 | 35 | 24 | Plant room | 5
SNS04 | N | MT-PLANTRM | Plant room humidity | RH | RH | 0 | 100 | 30 | 75 | 55 | Plant room | 5
SNS05 | N | FT-MU | Make-up water flow | Flow | m3h | -10 | 2000 | 0 | 1500 | 300 | Plant room | 5
SNS06 | N | KW-AUX | Auxiliary board power | Power | kW | -10 | 2000 | 0 | 1500 | 50 | Plant room | 5

## AirSide
Unit | Floor | Installed | Zones | Description
AHU_F02 | 2 | Y | 4 | Floor 2 air handling unit
AHU_F03 | 3 | Y | 4 | Floor 3 air handling unit
AHU_F04 | 4 | Y | 4 | Floor 4 air handling unit
AHU_F05 | 5 | Y | 4 | Floor 5 air handling unit
AHU_F06 | 6 | Y | 4 | Floor 6 air handling unit
AHU_F07 | 7 | Y | 4 | Floor 7 air handling unit
AHU_F08 | 8 | Y | 4 | Floor 8 air handling unit

## Systems
System | Tag | Type | Floor | X | Y | Z | Point | Note
fire_alarm | FACP-01 | panel | 1 | 3000 | 16000 | 1200 | FireAlarmSignal | Fire alarm control panel general alarm (already in the station)