## BOQ
ลำดับ | หมวด | รายการ | หน่วย | ปริมาณ | ค่าวัสดุ/หน่วย (บาท) | ค่าแรง/หน่วย (บาท) | รวมค่าวัสดุ | รวมค่าแรง | รวม (บาท)
1 | 1 ท่อ / Pipe | ท่อเหล็กดำ ASTM A53 Sch.40 Ø18" — CDR Condenser water return | m | 118.83
2 | 1 ท่อ / Pipe | ท่อเหล็กดำ ASTM A53 Sch.40 Ø8" — CDR Condenser water return | m | 31.02
3 | 1 ท่อ / Pipe | ท่อเหล็กดำ ASTM A53 Sch.40 Ø18" — CDS Condenser water supply | m | 157
4 | 1 ท่อ / Pipe | ท่อเหล็กดำ ASTM A53 Sch.40 Ø8" — CDS Condenser water supply | m | 15.88
5 | 1 ท่อ / Pipe | ท่อเหล็กดำ ASTM A53 Sch.40 Ø16" — CHR Chilled water return | m | 91.48
6 | 1 ท่อ / Pipe | ท่อเหล็กดำ ASTM A53 Sch.40 Ø8" — CHR Chilled water return | m | 8.62
7 | 1 ท่อ / Pipe | ท่อเหล็กดำ ASTM A53 Sch.40 Ø4" — CHR Chilled water return | m | 58.06
8 | 1 ท่อ / Pipe | ท่อเหล็กดำ ASTM A53 Sch.40 Ø2" — CHR Chilled water return | m | 1.12
9 | 1 ท่อ / Pipe | ท่อเหล็กดำ ASTM A53 Sch.40 Ø16" — CHS Chilled water supply | m | 74.2
10 | 1 ท่อ / Pipe | ท่อเหล็กดำ ASTM A53 Sch.40 Ø8" — CHS Chilled water supply | m | 6.37
11 | 1 ท่อ / Pipe | ท่อเหล็กดำ ASTM A53 Sch.40 Ø6" — CHS Chilled water supply | m | 4.91
12 | 1 ท่อ / Pipe | ท่อเหล็กดำ ASTM A53 Sch.40 Ø4" — CHS Chilled water supply | m | 41.9
13 | 2 ฉนวน / Insulation | ฉนวนยางสังเคราะห์ 25 มม. + แผ่นอะลูมิเนียมหุ้ม ท่อ Ø16" | m | 165.68
14 | 2 ฉนวน / Insulation | ฉนวนยางสังเคราะห์ 25 มม. + แผ่นอะลูมิเนียมหุ้ม ท่อ Ø8" | m | 14.99
15 | 2 ฉนวน / Insulation | ฉนวนยางสังเคราะห์ 25 มม. + แผ่นอะลูมิเนียมหุ้ม ท่อ Ø6" | m | 4.91
16 | 2 ฉนวน / Insulation | ฉนวนยางสังเคราะห์ 25 มม. + แผ่นอะลูมิเนียมหุ้ม ท่อ Ø4" | m | 99.96
17 | 2 ฉนวน / Insulation | ฉนวนยางสังเคราะห์ 25 มม. + แผ่นอะลูมิเนียมหุ้ม ท่อ Ø2" | m | 1.12
18 | 3 ข้อต่อ / Fittings | ข้องอ 90° long radius Ø18" | ea | 3
19 | 3 ข้อต่อ / Fittings | ข้องอ 90° long radius Ø16" | ea | 1
20 | 3 ข้อต่อ / Fittings | ข้องอ 90° long radius Ø8" | ea | 16
21 | 3 ข้อต่อ / Fittings | ข้องอ 90° long radius Ø6" | ea | 3
22 | 3 ข้อต่อ / Fittings | ข้องอ 90° long radius Ø4" | ea | 28
23 | 3 ข้อต่อ / Fittings | ข้องอ 90° long radius Ø2" | ea | 2
24 | 3 ข้อต่อ / Fittings | สามทาง Ø18" | ea | 1
25 | 3 ข้อต่อ / Fittings | สามทาง ลด Ø18"x8" | ea | 16
26 | 3 ข้อต่อ / Fittings | สามทาง Ø16" | ea | 1
27 | 3 ข้อต่อ / Fittings | สามทาง ลด Ø16"x6" | ea | 2
28 | 3 ข้อต่อ / Fittings | สามทาง ลด Ø16"x2" | ea | 1
29 | 3 ข้อต่อ / Fittings | สามทาง ลด Ø16"x8" | ea | 8
30 | 3 ข้อต่อ / Fittings | สามทาง ลด Ø16"x4" | ea | 13
31 | 4 วาล์ว / Valves | Automatic air vent 3/4" c/w isolating ball valve Ø16" | ea | 2
32 | 4 วาล์ว / Valves | Butterfly valve, lug type, PN16 Ø8" | ea | 12
33 | 4 วาล์ว / Valves | Butterfly valve, lug type, PN16 Ø6" | ea | 2
34 | 4 วาล์ว / Valves | Butterfly valve, lug type, PN16 Ø4" | ea | 7
35 | 4 วาล์ว / Valves | Butterfly valve, lug type, PN16 Ø2" | ea | 1
36 | 3 ข้อต่อ / Fittings | End cap / blind flange (header stub) Ø18" | set | 7
37 | 3 ข้อต่อ / Fittings | End cap / blind flange (header stub) Ø16" | set | 7
38 | 4 วาล์ว / Valves | Check valve, silent / dual plate Ø8" | ea | 4
39 | 4 วาล์ว / Valves | Drain valve 1-1/2" c/w hose cap Ø1.5" | ea | 2
40 | 4 วาล์ว / Valves | Flexible connector, EPDM double sphere Ø8" | ea | 12
41 | 4 วาล์ว / Valves | Flexible connector, EPDM double sphere Ø6" | ea | 4
42 | 5 เครื่องมือวัด / Instruments | Electromagnetic flow meter Ø18" | ea | 1
43 | 5 เครื่องมือวัด / Instruments | Electromagnetic flow meter Ø16" | ea | 1
44 | 5 เครื่องมือวัด / Instruments | Paddle flow switch Ø8" | ea | 4
45 | 4 วาล์ว / Valves | Motorized butterfly valve (on/off, 24 Vac) Ø8" | ea | 20
46 | 4 วาล์ว / Valves | Motorized control valve (modulating 0-10 V, position feedback) Ø8" | ea | 4
47 | 4 วาล์ว / Valves | Motorized control valve (modulating 0-10 V, position feedback) Ø6" | ea | 1
48 | 4 วาล์ว / Valves | Motorized control valve (modulating 0-10 V, position feedback) Ø4" | ea | 7
49 | 5 เครื่องมือวัด / Instruments | Pressure gauge 0-10 bar c/w cock Ø16" | ea | 1
50 | 5 เครื่องมือวัด / Instruments | Differential pressure transmitter 0-4 bar Ø16" | ea | 1
51 | 4 วาล์ว / Valves | Y-strainer, 20 mesh Ø8" | ea | 4
52 | 5 เครื่องมือวัด / Instruments | Temperature sensor 10k thermistor in well + thermometer Ø18" | ea | 2
53 | 5 เครื่องมือวัด / Instruments | Temperature sensor 10k thermistor in well + thermometer Ø16" | ea | 2
54 | 5 เครื่องมือวัด / Instruments | Temperature sensor 10k thermistor in well + thermometer Ø8" | ea | 2
55 | 3 ข้อต่อ / Fittings | หน้าแปลนเชื่อม PN16 Ø18" + ปะเก็น + สลักเกลียว | pair | 2
56 | 3 ข้อต่อ / Fittings | หน้าแปลนเชื่อม PN16 Ø16" + ปะเก็น + สลักเกลียว | pair | 2
57 | 3 ข้อต่อ / Fittings | หน้าแปลนเชื่อม PN16 Ø8" + ปะเก็น + สลักเกลียว | pair | 136
58 | 3 ข้อต่อ / Fittings | หน้าแปลนเชื่อม PN16 Ø6" + ปะเก็น + สลักเกลียว | pair | 14
59 | 3 ข้อต่อ / Fittings | หน้าแปลนเชื่อม PN16 Ø4" + ปะเก็น + สลักเกลียว | pair | 42
60 | 3 ข้อต่อ / Fittings | หน้าแปลนเชื่อม PN16 Ø2" + ปะเก็น + สลักเกลียว | pair | 3
61 | 6 ที่รองรับท่อ / Supports | Floor pipe stanchion + base plate สำหรับท่อ Ø2" | set | 0
62 | 6 ที่รองรับท่อ / Supports | Floor pipe stanchion + base plate สำหรับท่อ Ø6" | set | 1
63 | 6 ที่รองรับท่อ / Supports | Floor pipe stanchion + base plate สำหรับท่อ Ø8" | set | 6
64 | 6 ที่รองรับท่อ / Supports | Floor pipe stanchion + base plate สำหรับท่อ Ø16" | set | 5
65 | 6 ที่รองรับท่อ / Supports | Floor pipe stanchion + base plate สำหรับท่อ Ø18" | set | 6
66 | 6 ที่รองรับท่อ / Supports | Pipe hanger (rod Ø12 + clevis) สำหรับท่อ Ø4" | set | 28
67 | 6 ที่รองรับท่อ / Supports | Pipe hanger (rod Ø12 + clevis) สำหรับท่อ Ø16" | set | 27
68 | 6 ที่รองรับท่อ / Supports | Pipe hanger (rod Ø12 + clevis) สำหรับท่อ Ø18" | set | 30
69 | 6 ที่รองรับท่อ / Supports | Riser clamp สำหรับท่อ Ø2" | set | 0
70 | 6 ที่รองรับท่อ / Supports | Riser clamp สำหรับท่อ Ø4" | set | 0
71 | 6 ที่รองรับท่อ / Supports | Riser clamp สำหรับท่อ Ø6" | set | 0
72 | 6 ที่รองรับท่อ / Supports | Riser clamp สำหรับท่อ Ø8" | set | 0
73 | 6 ที่รองรับท่อ / Supports | Riser clamp สำหรับท่อ Ø16" | set | 0
74 | 6 ที่รองรับท่อ / Supports | Riser clamp สำหรับท่อ Ø18" | set | 3
75 | 6 ที่รองรับท่อ / Supports | Roof pipe sleeper (concrete block + saddle) สำหรับท่อ Ø8" | set | 8
76 | 6 ที่รองรับท่อ / Supports | Roof pipe sleeper (concrete block + saddle) สำหรับท่อ Ø18" | set | 37
77 | 7 งานสี / Painting | แถบสีบริการ + ลูกศรทิศทางการไหล (ทุก 3 ม.) | set | 181
78 | 8 อุปกรณ์ / Equipment | CH-01 — Water-cooled screw / centrifugal (reference) | set | 1
79 | 8 อุปกรณ์ / Equipment | CH-02 — Water-cooled screw / centrifugal (reference) | set | 1
80 | 8 อุปกรณ์ / Equipment | CHP-01 — Chilled water pump (primary-variable, headered) | set | 1
81 | 8 อุปกรณ์ / Equipment | CHP-02 — Chilled water pump (primary-variable, headered) | set | 1
82 | 8 อุปกรณ์ / Equipment | CDP-01 — Condenser water pump (headered) | set | 1
83 | 8 อุปกรณ์ / Equipment | CDP-02 — Condenser water pump (headered) | set | 1
84 | 8 อุปกรณ์ / Equipment | CT-01/1 — Cooling tower cell, Crossflow, induced draft (FRP) | set | 1
85 | 8 อุปกรณ์ / Equipment | CT-01/2 — Cooling tower cell, Crossflow, induced draft (FRP) | set | 1
86 | 8 อุปกรณ์ / Equipment | CT-02/1 — Cooling tower cell, Crossflow, induced draft (FRP) | set | 1
87 | 8 อุปกรณ์ / Equipment | CT-02/2 — Cooling tower cell, Crossflow, induced draft (FRP) | set | 1
88 | 8 อุปกรณ์ / Equipment | ET-01 — Expansion tank | set | 1
89 | 8 อุปกรณ์ / Equipment | DPB-01 — CHW minimum-flow bypass | set | 1
90 | 8 อุปกรณ์ / Equipment | CP-01 — CPMS control panel (Niagara JACE / Supervisor) | set | 1
91 | 8 อุปกรณ์ / Equipment | AHU-01 — Cooling tower cell, Air handling unit, CHW coil, VSD fan | set | 1
92 | 8 อุปกรณ์ / Equipment | AHU-02 — Cooling tower cell, Air handling unit, CHW coil, VSD fan | set | 1
93 | 8 อุปกรณ์ / Equipment | OAU-01 — Cooling tower cell, Outdoor air unit (dew point control) | set | 1
94 | 8 อุปกรณ์ / Equipment | FCU-01 — Cooling tower cell, Fan coil unit, 3-speed fan, on/off valve | set | 1
95 | 8 อุปกรณ์ / Equipment | FCU-02 — Cooling tower cell, Fan coil unit, 3-speed fan, on/off valve | set | 1
96 | 8 อุปกรณ์ / Equipment | FCU-03 — Cooling tower cell, Fan coil unit, 3-speed fan, on/off valve | set | 1
97 | 8 อุปกรณ์ / Equipment | FCU-04 — Cooling tower cell, Fan coil unit, 3-speed fan, on/off valve | set | 1
98 | 8 อุปกรณ์ / Equipment | AHU-F02 — Cooling tower cell, Air handling unit, CHW coil, VSD fan | set | 1
99 | 8 อุปกรณ์ / Equipment | AHU-F03 — Cooling tower cell, Air handling unit, CHW coil, VSD fan | set | 1
100 | 8 อุปกรณ์ / Equipment | AHU-F04 — Cooling tower cell, Air handling unit, CHW coil, VSD fan | set | 1
101 | 8 อุปกรณ์ / Equipment | AHU-F05 — Cooling tower cell, Air handling unit, CHW coil, VSD fan | set | 1
102 | 8 อุปกรณ์ / Equipment | AHU-F06 — Cooling tower cell, Air handling unit, CHW coil, VSD fan | set | 1
103 | 8 อุปกรณ์ / Equipment | AHU-F07 — Cooling tower cell, Air handling unit, CHW coil, VSD fan | set | 1
104 | 8 อุปกรณ์ / Equipment | AHU-F08 — Cooling tower cell, Air handling unit, CHW coil, VSD fan | set | 1
105 | 8 อุปกรณ์ / Equipment | EF-01 — Cooling tower cell, Fan | set | 1
106 | 8 อุปกรณ์ / Equipment | EF-02 — Cooling tower cell, Fan | set | 1
107 | 8 อุปกรณ์ / Equipment | EF-03 — Cooling tower cell, Fan | set | 1
108 | 8 อุปกรณ์ / Equipment | CPEF-01 — Cooling tower cell, Fan | set | 1
109 | 8 อุปกรณ์ / Equipment | LSF-01 — Cooling tower cell, Fan | set | 1
110 | 8 อุปกรณ์ / Equipment | SEF-01 — Cooling tower cell, Fan | set | 1
รวมก่อนภาษี / SUBTOTAL
ภาษีมูลค่าเพิ่ม 7% / VAT
รวมทั้งสิ้น / GRAND TOTAL
ช่องสีเหลือง = ราคาต่อหน่วยให้ผู้ประมาณราคากรอก · ปริมาณคำนวณอัตโนมัติจากแบบจำลอง BIM (ท่อ +5% เผื่อเศษ) · สร้างใหม่ได้ทุกครั้งที่แก้แบบจำลอง
IFC: ALT_Lotus_ChillerPlant.ifc · Drawing set M-000…M-601 · generated 08/10/2026

## Pipe runs
Pipe ID | Service | DN (in) | Length (m) | Elbows | Insulated | Capped ends | Flow-span (m) | Status point | Note
CHR-R | CHR | 16 | 33.68 | 0 | Y | start | 4.20-33.68 | Gfx_ChwMain_Fwd | CHW return riser (shaft)
CHR-SH | CHR | 16 | 12.9 | 0 | Y | end | 0.00-12.00 | Gfx_ChwMain_Fwd | CHP suction header
CHR-DH | CHR | 16 | 11.2 | 0 | Y | both | 0.90-7.70 | Gfx_EvapTotal_Fwd | CHP discharge header
CHR-EH | CHR | 16 | 29.34 | 0 | Y | end | 0.00-29.05 | Gfx_EvapTotal_Fwd | CHW header to evaporators
CHS-H | CHS | 16 | 39.67 | 1 | Y | start | 0.30-39.67 | Gfx_ChwMain_Fwd | CHW supply header
CHS-R | CHS | 16 | 31 | 0 | Y | end | 0.00-30.70 | Gfx_ChwMain_Fwd | CHW supply riser (shaft)
CHW-BP | CHS | 6 | 4.68 | 3 | Y |  | 0.00-4.68 | Gfx_Bypass_Fwd | minimum-flow bypass
CHW-ET | CHR | 2 | 1.07 | 2 | Y |  | 0.00-1.07 |  | expansion tank
CDS-RH | CDS | 18 | 50.1 | 1 |  | start | 0.30-50.10 | Gfx_CdwTotal_Fwd | roof collecting header
CDS-R | CDS | 18 | 34.73 | 0 |  |  | 0.00-34.73 | Gfx_CdwTotal_Fwd | CDW riser from the towers
CDS-SH | CDS | 18 | 17.3 | 1 |  | end | 0.00-16.40 | Gfx_CdwTotal_Fwd | CDP suction header
CDS-DH | CDS | 18 | 11.2 | 0 |  | both | 0.90-6.40 | Gfx_CdwTotal_Fwd | CDP discharge header
CDS-CH | CDS | 18 | 36.2 | 0 |  | end | 0.00-35.90 | Gfx_CdwTotal_Fwd | CDW header to condensers
CDR-H | CDR | 18 | 39.92 | 0 |  | start | 0.30-39.92 | Gfx_CdwTotal_Fwd | CDW return header
CDR-R | CDR | 18 | 33.35 | 1 |  |  | 0.00-33.35 | Gfx_CdwTotal_Fwd | CDW return riser to the roof
CDR-RH | CDR | 18 | 39.9 | 0 |  | end | 0.00-39.60 | Gfx_CdwTotal_Fwd | roof distribution header
CHR-E1 | CHR | 8 | 1.83 | 1 | Y |  | 0.00-1.83 | Gfx_CH01Evap_Fwd
CHS-E1 | CHS | 8 | 3.03 | 1 | Y |  | 0.00-3.03 | Gfx_CH01Evap_Fwd
CDS-C1 | CDS | 8 | 2.79 | 1 |  |  | 0.00-2.79 | Gfx_CH01Cond_Fwd
CDR-C1 | CDR | 8 | 5.59 | 1 |  |  | 0.00-5.59 | Gfx_CH01Cond_Fwd
CHR-E2 | CHR | 8 | 1.83 | 1 | Y |  | 0.00-1.83 | Gfx_CH02Evap_Fwd
CHS-E2 | CHS | 8 | 3.03 | 1 | Y |  | 0.00-3.03 | Gfx_CH02Evap_Fwd
CDS-C2 | CDS | 8 | 2.79 | 1 |  |  | 0.00-2.79 | Gfx_CH02Cond_Fwd
CDR-C2 | CDR | 8 | 5.59 | 1 |  |  | 0.00-5.59 | Gfx_CH02Cond_Fwd
CHR-P1 | CHR | 8 | 0.78 | 0 | Y |  | 0.00-0.78 | Gfx_CHP01_Fwd
CHR-D1 | CHR | 8 | 1.49 | 0 | Y |  | 0.00-1.49 | Gfx_CHP01_Fwd
CHR-P2 | CHR | 8 | 0.78 | 0 | Y |  | 0.00-0.78 | Gfx_CHP02_Fwd
CHR-D2 | CHR | 8 | 1.49 | 0 | Y |  | 0.00-1.49 | Gfx_CHP02_Fwd
CDS-P1 | CDS | 8 | 0.38 | 0 |  |  | 0.00-0.38 | Gfx_CDP01_Fwd
CDS-D1 | CDS | 8 | 0.69 | 0 |  |  | 0.00-0.69 | Gfx_CDP01_Fwd
CDS-P2 | CDS | 8 | 0.38 | 0 |  |  | 0.00-0.38 | Gfx_CDP02_Fwd
CDS-D2 | CDS | 8 | 0.69 | 0 |  |  | 0.00-0.69 | Gfx_CDP02_Fwd
CDR-T1 | CDR | 8 | 4.59 | 1 |  |  | 0.00-4.59 | Gfx_CT01_Fwd | cell inlet
CDS-T1 | CDS | 8 | 1.85 | 1 |  |  | 0.00-1.85 | Gfx_CT01_Fwd | cell outlet
CDR-T2 | CDR | 8 | 4.59 | 1 |  |  | 0.00-4.59 | Gfx_CT01_Fwd | cell inlet
CDS-T2 | CDS | 8 | 1.85 | 1 |  |  | 0.00-1.85 | Gfx_CT01_Fwd | cell outlet
CDR-T3 | CDR | 8 | 4.59 | 1 |  |  | 0.00-4.59 | Gfx_CT02_Fwd | cell inlet
CDS-T3 | CDS | 8 | 1.85 | 1 |  |  | 0.00-1.85 | Gfx_CT02_Fwd | cell outlet
CDR-T4 | CDR | 8 | 4.59 | 1 |  |  | 0.00-4.59 | Gfx_CT02_Fwd | cell inlet
CDS-T4 | CDS | 8 | 1.85 | 1 |  |  | 0.00-1.85 | Gfx_CT02_Fwd | cell outlet
CHS-F2 | CHS | 4 | 5.7 | 2 | Y |  | 0.00-5.70 | Gfx_AHU_F02_Fwd | floor 2 AHU supply
CHR-F2 | CHR | 4 | 7.9 | 2 | Y |  | 0.00-7.90 | Gfx_AHU_F02_Fwd | floor 2 AHU return
CHS-F3 | CHS | 4 | 5.7 | 2 | Y |  | 0.00-5.70 | Gfx_AHU_F03_Fwd | floor 3 AHU supply
CHR-F3 | CHR | 4 | 7.9 | 2 | Y |  | 0.00-7.90 | Gfx_AHU_F03_Fwd | floor 3 AHU return
CHS-F4 | CHS | 4 | 5.7 | 2 | Y |  | 0.00-5.70 | Gfx_AHU_F04_Fwd | floor 4 AHU supply
CHR-F4 | CHR | 4 | 7.9 | 2 | Y |  | 0.00-7.90 | Gfx_AHU_F04_Fwd | floor 4 AHU return
CHS-F5 | CHS | 4 | 5.7 | 2 | Y |  | 0.00-5.70 | Gfx_AHU_F05_Fwd | floor 5 AHU supply
CHR-F5 | CHR | 4 | 7.9 | 2 | Y |  | 0.00-7.90 | Gfx_AHU_F05_Fwd | floor 5 AHU return
CHS-F6 | CHS | 4 | 5.7 | 2 | Y |  | 0.00-5.70 | Gfx_AHU_F06_Fwd | floor 6 AHU supply
CHR-F6 | CHR | 4 | 7.9 | 2 | Y |  | 0.00-7.90 | Gfx_AHU_F06_Fwd | floor 6 AHU return
CHS-F7 | CHS | 4 | 5.7 | 2 | Y |  | 0.00-5.70 | Gfx_AHU_F07_Fwd | floor 7 AHU supply
CHR-F7 | CHR | 4 | 7.9 | 2 | Y |  | 0.00-7.90 | Gfx_AHU_F07_Fwd | floor 7 AHU return
CHS-F8 | CHS | 4 | 5.7 | 2 | Y |  | 0.00-5.70 | Gfx_AHU_F08_Fwd | floor 8 AHU supply
CHR-F8 | CHR | 4 | 7.9 | 2 | Y |  | 0.00-7.90 | Gfx_AHU_F08_Fwd | floor 8 AHU return

## Valves & instruments
# | Kind | Description | DN (in) | Pipe | Distance along pipe (mm) | X | Y | Z | Tag | BMS point
1 | MBFV | Motorized butterfly valve (on/off, 24 Vac) | 8 | CHR-P1 | 150 | 32450 | 1600 | 620 | CHP01 suction | Gfx_CHP01_SuctionMV_Pos
2 | STRAINER | Y-strainer, 20 mesh | 8 | CHR-P1 | 420 | 32720 | 1600 | 620
3 | FLEX | Flexible connector, EPDM double sphere | 6 | CHR-P1 | -160 | 32920 | 1600 | 620
4 | FLEX | Flexible connector, EPDM double sphere | 8 | CHR-D1 | 140 | 33475 | 1600 | 1250
5 | CHECK | Check valve, silent / dual plate | 8 | CHR-D1 | 420 | 33475 | 1600 | 1530
6 | MBFV | Motorized butterfly valve (on/off, 24 Vac) | 8 | CHR-D1 | 760 | 33475 | 1600 | 1870 | CHP01 discharge MV | Gfx_CHP01_DischargeMV_Pos
7 | MBFV | Motorized butterfly valve (on/off, 24 Vac) | 8 | CHR-P2 | 150 | 32450 | 3600 | 620 | CHP02 suction | Gfx_CHP02_SuctionMV_Pos
8 | STRAINER | Y-strainer, 20 mesh | 8 | CHR-P2 | 420 | 32720 | 3600 | 620
9 | FLEX | Flexible connector, EPDM double sphere | 6 | CHR-P2 | -160 | 32920 | 3600 | 620
10 | FLEX | Flexible connector, EPDM double sphere | 8 | CHR-D2 | 140 | 33475 | 3600 | 1250
11 | CHECK | Check valve, silent / dual plate | 8 | CHR-D2 | 420 | 33475 | 3600 | 1530
12 | MBFV | Motorized butterfly valve (on/off, 24 Vac) | 8 | CHR-D2 | 760 | 33475 | 3600 | 1870 | CHP02 discharge MV | Gfx_CHP02_DischargeMV_Pos
13 | MBFV | Motorized butterfly valve (on/off, 24 Vac) | 8 | CDS-P1 | 150 | 38850 | 1600 | 620 | CDP01 suction | Gfx_CDP01_SuctionMV_Pos
14 | STRAINER | Y-strainer, 20 mesh | 8 | CDS-P1 | 420 | 39080 | 1600 | 620
15 | FLEX | Flexible connector, EPDM double sphere | 6 | CDS-P1 | -160 | 38920 | 1600 | 620
16 | FLEX | Flexible connector, EPDM double sphere | 8 | CDS-D1 | 140 | 39475 | 1600 | 1250
17 | CHECK | Check valve, silent / dual plate | 8 | CDS-D1 | 420 | 39475 | 1600 | 1530
18 | MBFV | Motorized butterfly valve (on/off, 24 Vac) | 8 | CDS-D1 | 760 | 39475 | 1600 | 1800 | CDP01 discharge MV | Gfx_CDP01_DischargeMV_Pos
19 | MBFV | Motorized butterfly valve (on/off, 24 Vac) | 8 | CDS-P2 | 150 | 38850 | 3600 | 620 | CDP02 suction | Gfx_CDP02_SuctionMV_Pos
20 | STRAINER | Y-strainer, 20 mesh | 8 | CDS-P2 | 420 | 39080 | 3600 | 620
21 | FLEX | Flexible connector, EPDM double sphere | 6 | CDS-P2 | -160 | 38920 | 3600 | 620
22 | FLEX | Flexible connector, EPDM double sphere | 8 | CDS-D2 | 140 | 39475 | 3600 | 1250
23 | CHECK | Check valve, silent / dual plate | 8 | CDS-D2 | 420 | 39475 | 3600 | 1530
24 | MBFV | Motorized butterfly valve (on/off, 24 Vac) | 8 | CDS-D2 | 760 | 39475 | 3600 | 1800 | CDP02 discharge MV | Gfx_CDP02_DischargeMV_Pos
25 | BFV | Butterfly valve, lug type, PN16 | 8 | CHR-E1 | 400 | 4430 | 8400 | 2200
26 | MBFV | Motorized butterfly valve (on/off, 24 Vac) | 8 | CHR-E1 | -260 | 4430 | 8553 | 1180 | CH01 CHW isolation | Gfx_CH01_ChwIso_Pos
27 | FLEX | Flexible connector, EPDM double sphere | 8 | CHR-E1 | -120 | 4430 | 8693 | 1180
28 | FLEX | Flexible connector, EPDM double sphere | 8 | CHS-E1 | 150 | 3930 | 8663 | 1180
29 | TT | Temperature sensor 10k thermistor in well + thermometer | 8 | CHS-E1 | 330 | 3930 | 8483 | 1180 |  | CH01_ChwSupplyTemp
30 | FS | Paddle flow switch | 8 | CHS-E1 | 520 | 3930 | 8293 | 1180 | CH01 evaporator flow switch
31 | MCV | Motorized control valve (modulating 0-10 V, position feedback) | 8 | CHS-E1 | 900 | 3930 | 7913 | 1180 | CH01 CHW flow control | Gfx_CH01_ChwFCV_Pos
32 | BFV | Butterfly valve, lug type, PN16 | 8 | CDS-C1 | 400 | 3580 | 7100 | 1400
33 | MBFV | Motorized butterfly valve (on/off, 24 Vac) | 8 | CDS-C1 | -260 | 3580 | 8553 | 720 | CH01 CDW isolation | Gfx_CH01_CdwIso_Pos
34 | FLEX | Flexible connector, EPDM double sphere | 8 | CDS-C1 | -120 | 3580 | 8693 | 720
35 | FLEX | Flexible connector, EPDM double sphere | 8 | CDR-C1 | 150 | 3980 | 8663 | 720
36 | FS | Paddle flow switch | 8 | CDR-C1 | 520 | 3980 | 8293 | 720 | CH01 condenser flow switch
37 | MCV | Motorized control valve (modulating 0-10 V, position feedback) | 8 | CDR-C1 | 1000 | 3980 | 7813 | 720 | CH01 head-pressure valve | Gfx_CH01_CdwHPV_Pos
38 | BFV | Butterfly valve, lug type, PN16 | 8 | CHR-E2 | 400 | 9430 | 8400 | 2200
39 | MBFV | Motorized butterfly valve (on/off, 24 Vac) | 8 | CHR-E2 | -260 | 9430 | 8553 | 1180 | CH02 CHW isolation | Gfx_CH02_ChwIso_Pos
40 | FLEX | Flexible connector, EPDM double sphere | 8 | CHR-E2 | -120 | 9430 | 8693 | 1180
41 | FLEX | Flexible connector, EPDM double sphere | 8 | CHS-E2 | 150 | 8930 | 8663 | 1180
42 | TT | Temperature sensor 10k thermistor in well + thermometer | 8 | CHS-E2 | 330 | 8930 | 8483 | 1180 |  | CH02_ChwSupplyTemp
43 | FS | Paddle flow switch | 8 | CHS-E2 | 520 | 8930 | 8293 | 1180 | CH02 evaporator flow switch
44 | MCV | Motorized control valve (modulating 0-10 V, position feedback) | 8 | CHS-E2 | 900 | 8930 | 7913 | 1180 | CH02 CHW flow control | Gfx_CH02_ChwFCV_Pos
45 | BFV | Butterfly valve, lug type, PN16 | 8 | CDS-C2 | 400 | 8580 | 7100 | 1400
46 | MBFV | Motorized butterfly valve (on/off, 24 Vac) | 8 | CDS-C2 | -260 | 8580 | 8553 | 720 | CH02 CDW isolation | Gfx_CH02_CdwIso_Pos
47 | FLEX | Flexible connector, EPDM double sphere | 8 | CDS-C2 | -120 | 8580 | 8693 | 720
48 | FLEX | Flexible connector, EPDM double sphere | 8 | CDR-C2 | 150 | 8980 | 8663 | 720
49 | FS | Paddle flow switch | 8 | CDR-C2 | 520 | 8980 | 8293 | 720 | CH02 condenser flow switch
50 | MCV | Motorized control valve (modulating 0-10 V, position feedback) | 8 | CDR-C2 | 1000 | 8980 | 7813 | 720 | CH02 head-pressure valve | Gfx_CH02_CdwHPV_Pos
51 | BFV | Butterfly valve, lug type, PN16 | 8 | CDR-T1 | 400 | 4000 | 8200 | 36450
52 | MBFV | Motorized butterfly valve (on/off, 24 Vac) | 8 | CDR-T1 | 900 | 4000 | 8200 | 36950 | CT01 inlet | Gfx_CT01_InletMV_Pos
53 | MBFV | Motorized butterfly valve (on/off, 24 Vac) | 8 | CDS-T1 | 250 | 3300 | 4450 | 36100 | CT01 outlet | Gfx_CT01_OutletMV_Pos
54 | BFV | Butterfly valve, lug type, PN16 | 8 | CDS-T1 | 700 | 3300 | 4000 | 36100
55 | BFV | Butterfly valve, lug type, PN16 | 8 | CDR-T2 | 400 | 6800 | 8200 | 36450
56 | MBFV | Motorized butterfly valve (on/off, 24 Vac) | 8 | CDR-T2 | 900 | 6800 | 8200 | 36950 | CT01 inlet | Gfx_CT01_InletMV_Pos
57 | MBFV | Motorized butterfly valve (on/off, 24 Vac) | 8 | CDS-T2 | 250 | 6100 | 4450 | 36100 | CT01 outlet | Gfx_CT01_OutletMV_Pos
58 | BFV | Butterfly valve, lug type, PN16 | 8 | CDS-T2 | 700 | 6100 | 4000 | 36100
59 | BFV | Butterfly valve, lug type, PN16 | 8 | CDR-T3 | 400 | 9600 | 8200 | 36450
60 | MBFV | Motorized butterfly valve (on/off, 24 Vac) | 8 | CDR-T3 | 900 | 9600 | 8200 | 36950 | CT02 inlet | Gfx_CT02_InletMV_Pos
61 | MBFV | Motorized butterfly valve (on/off, 24 Vac) | 8 | CDS-T3 | 250 | 8900 | 4450 | 36100 | CT02 outlet | Gfx_CT02_OutletMV_Pos
62 | BFV | Butterfly valve, lug type, PN16 | 8 | CDS-T3 | 700 | 8900 | 4000 | 36100
63 | BFV | Butterfly valve, lug type, PN16 | 8 | CDR-T4 | 400 | 12400 | 8200 | 36450
64 | MBFV | Motorized butterfly valve (on/off, 24 Vac) | 8 | CDR-T4 | 900 | 12400 | 8200 | 36950 | CT02 inlet | Gfx_CT02_InletMV_Pos
65 | MBFV | Motorized butterfly valve (on/off, 24 Vac) | 8 | CDS-T4 | 250 | 11700 | 4450 | 36100 | CT02 outlet | Gfx_CT02_OutletMV_Pos
66 | BFV | Butterfly valve, lug type, PN16 | 8 | CDS-T4 | 700 | 11700 | 4000 | 36100
67 | MCV | Motorized control valve (modulating 0-10 V, position feedback) | 4 | CHS-F2 | -300 | 36400 | 17500 | 7300 | AHU_F02 CHW valve | AHU_F02_ValveCmd
68 | BFV | Butterfly valve, lug type, PN16 | 4 | CHR-F2 | 300 | 33600 | 17500 | 6700
69 | MCV | Motorized control valve (modulating 0-10 V, position feedback) | 4 | CHS-F3 | -300 | 36400 | 17500 | 11500 | AHU_F03 CHW valve | AHU_F03_ValveCmd
70 | BFV | Butterfly valve, lug type, PN16 | 4 | CHR-F3 | 300 | 33600 | 17500 | 10900
71 | MCV | Motorized control valve (modulating 0-10 V, position feedback) | 4 | CHS-F4 | -300 | 36400 | 17500 | 15700 | AHU_F04 CHW valve | AHU_F04_ValveCmd
72 | BFV | Butterfly valve, lug type, PN16 | 4 | CHR-F4 | 300 | 33600 | 17500 | 15100
73 | MCV | Motorized control valve (modulating 0-10 V, position feedback) | 4 | CHS-F5 | -300 | 36400 | 17500 | 19900 | AHU_F05 CHW valve | AHU_F05_ValveCmd
74 | BFV | Butterfly valve, lug type, PN16 | 4 | CHR-F5 | 300 | 33600 | 17500 | 19300
75 | MCV | Motorized control valve (modulating 0-10 V, position feedback) | 4 | CHS-F6 | -300 | 36400 | 17500 | 24100 | AHU_F06 CHW valve | AHU_F06_ValveCmd
76 | BFV | Butterfly valve, lug type, PN16 | 4 | CHR-F6 | 300 | 33600 | 17500 | 23500
77 | MCV | Motorized control valve (modulating 0-10 V, position feedback) | 4 | CHS-F7 | -300 | 36400 | 17500 | 28300 | AHU_F07 CHW valve | AHU_F07_ValveCmd
78 | BFV | Butterfly valve, lug type, PN16 | 4 | CHR-F7 | 300 | 33600 | 17500 | 27700
79 | MCV | Motorized control valve (modulating 0-10 V, position feedback) | 4 | CHS-F8 | -300 | 36400 | 17500 | 32500 | AHU_F08 CHW valve | AHU_F08_ValveCmd
80 | BFV | Butterfly valve, lug type, PN16 | 4 | CHR-F8 | 300 | 33600 | 17500 | 31900
81 | TT | Temperature sensor 10k thermistor in well + thermometer | 16 | CHS-H | 1500 | 5130 | 7900 | 3300 | CHWS | CHWS
82 | FM | Electromagnetic flow meter | 16 | CHS-H | 2200 | 5830 | 7900 | 3300 | CHWFlow | CHWFlow
83 | PT | Differential pressure transmitter 0-4 bar | 16 | CHS-R | 1500 | 37000 | 14200 | 4800 | CHWDP
84 | TT | Temperature sensor 10k thermistor in well + thermometer | 16 | CHR-R | -600 | 32300 | 13600 | 1220 | CHWR | CHWR
85 | PG | Pressure gauge 0-10 bar c/w cock | 16 | CHR-R | -900 | 32300 | 13600 | 1520
86 | BFV | Butterfly valve, lug type, PN16 | 6 | CHW-BP | 3000 | 31000 | 8600 | 1000
87 | MCV | Motorized control valve (modulating 0-10 V, position feedback) | 6 | CHW-BP | 3800 | 31800 | 8600 | 1000 | CHW bypass valve | Gfx_CHW_BypassMV_Pos
88 | BFV | Butterfly valve, lug type, PN16 | 6 | CHW-BP | 4600 | 32300 | 8600 | 700
89 | BFV | Butterfly valve, lug type, PN16 | 2 | CHW-ET | 120 | 31570 | 12900 | 400
90 | TT | Temperature sensor 10k thermistor in well + thermometer | 18 | CDS-SH | 1200 | 41300 | 14200 | 620 | CDS | CDS
91 | FM | Electromagnetic flow meter | 18 | CDS-CH | 1800 | 37675 | 7100 | 1800 | CDW_Flow | CDW_Flow
92 | TT | Temperature sensor 10k thermistor in well + thermometer | 18 | CDR-H | -1500 | 42100 | 6700 | 4200 | CDR | CDR
93 | CAP | End cap / blind flange (header stub) | 16 | CHR-R | 1 | 32300 | 13600 | 34299
94 | AAV | Automatic air vent 3/4" c/w isolating ball valve | 16 | CHR-R | 60 | 32300 | 13600 | 34240
95 | CAP | End cap / blind flange (header stub) | 16 | CHR-SH | -1 | 32300 | 701 | 620
96 | DRAIN | Drain valve 1-1/2" c/w hose cap | 1.5 | CHR-SH | -25 | 32300 | 725 | 620
97 | CAP | End cap / blind flange (header stub) | 16 | CHR-DH | 1 | 33475 | 701 | 2600
98 | CAP | End cap / blind flange (header stub) | 16 | CHR-DH | -1 | 33475 | 11899 | 2600
99 | CAP | End cap / blind flange (header stub) | 16 | CHR-EH | -1 | 4131 | 8400 | 2600
100 | CAP | End cap / blind flange (header stub) | 16 | CHS-H | 1 | 3631 | 7900 | 3300
101 | CAP | End cap / blind flange (header stub) | 16 | CHS-R | -1 | 37000 | 14200 | 34299
102 | AAV | Automatic air vent 3/4" c/w isolating ball valve | 16 | CHS-R | -60 | 37000 | 14200 | 34240
103 | CAP | End cap / blind flange (header stub) | 18 | CDS-RH | 1 | 3001 | 3600 | 35350
104 | CAP | End cap / blind flange (header stub) | 18 | CDS-SH | -1 | 38700 | 701 | 620
105 | DRAIN | Drain valve 1-1/2" c/w hose cap | 1.5 | CDS-SH | -25 | 38700 | 725 | 620
106 | CAP | End cap / blind flange (header stub) | 18 | CDS-DH | 1 | 39475 | 701 | 1800
107 | CAP | End cap / blind flange (header stub) | 18 | CDS-DH | -1 | 39475 | 11899 | 1800
108 | CAP | End cap / blind flange (header stub) | 18 | CDS-CH | -1 | 3281 | 7100 | 1800
109 | CAP | End cap / blind flange (header stub) | 18 | CDR-H | 1 | 3681 | 6700 | 4200
110 | CAP | End cap / blind flange (header stub) | 18 | CDR-RH | -1 | 3701 | 8200 | 36050

## Fittings
Fitting | Run DN | Branch DN | Qty
TEE | 16 | 16 | 1
TEE | 16 | 6 | 2
TEE | 16 | 2 | 1
TEE | 18 | 18 | 1
TEE | 16 | 8 | 8
TEE | 18 | 8 | 16
TEE | 16 | 4 | 13
ELBOW 90 LR | 16 |  | 1
ELBOW 90 LR | 6 |  | 3
ELBOW 90 LR | 2 |  | 2
ELBOW 90 LR | 18 |  | 3
ELBOW 90 LR | 8 |  | 16
ELBOW 90 LR | 4 |  | 28
FLANGE PAIR PN16 | 8 |  | 136
FLANGE PAIR PN16 | 6 |  | 14
FLANGE PAIR PN16 | 4 |  | 42
FLANGE PAIR PN16 | 16 |  | 2
FLANGE PAIR PN16 | 2 |  | 3
FLANGE PAIR PN16 | 18 |  | 2

## Supports
Support type | Pipe DN | Qty
Floor pipe stanchion + base plate | 2 | 0
Floor pipe stanchion + base plate | 6 | 1
Floor pipe stanchion + base plate | 8 | 6
Floor pipe stanchion + base plate | 16 | 5
Floor pipe stanchion + base plate | 18 | 6
Pipe hanger (rod Ø12 + clevis) | 4 | 28
Pipe hanger (rod Ø12 + clevis) | 16 | 27
Pipe hanger (rod Ø12 + clevis) | 18 | 30
Riser clamp | 2 | 0
Riser clamp | 4 | 0
Riser clamp | 6 | 0
Riser clamp | 8 | 0
Riser clamp | 16 | 0
Riser clamp | 18 | 3
Roof pipe sleeper (concrete block + saddle) | 8 | 8
Roof pipe sleeper (concrete block + saddle) | 18 | 37

## Equipment
Tag | Type | X | Y | Z | Rot | L | W | H | BMS point | Data
CH-01 | chiller | 4000 | 11000 | 100 | 90 | 3774 | 1771 | 2033 | CH01 | Model: Water-cooled screw / centrifugal (reference); Capacity: 334 TR; Efficiency: 0.614 kW/TR; CHW: 6.7 -> 12.2 C; Power: 380 V / 3 Ph / 50 Hz; Slot: CH01; Logic: V7.8 base unit
CH-02 | chiller | 9000 | 11000 | 100 | 90 | 3774 | 1771 | 2033 | CH02 | Model: Water-cooled screw / centrifugal (reference); Capacity: 334 TR; Efficiency: 0.614 kW/TR; CHW: 6.7 -> 12.2 C; Power: 380 V / 3 Ph / 50 Hz; Slot: CH02; Logic: V7.8 base unit
CHP-01 | pump | 34000 | 1600 | 0 | 0 | 1750 | 650 | 850 | CHP01 | Service: Chilled water pump (primary-variable, headered); Type: End suction, VSD; Flow: 800 USgpm; Head: 80 ft; Motor: 22 kW, 380/3/50; Slot: CHP01
CHP-02 | pump | 34000 | 3600 | 0 | 0 | 1750 | 650 | 850 | CHP02 | Service: Chilled water pump (primary-variable, headered); Type: End suction, VSD; Flow: 800 USgpm; Head: 80 ft; Motor: 22 kW, 380/3/50; Slot: CHP02
CDP-01 | pump | 40000 | 1600 | 0 | 0 | 1750 | 650 | 850 | CDP01 | Service: Condenser water pump (headered); Type: End suction, VSD; Flow: 1,000 USgpm; Head: 80 ft; Motor: 30 kW, 380/3/50; Slot: CDP01
CDP-02 | pump | 40000 | 3600 | 0 | 0 | 1750 | 650 | 850 | CDP02 | Service: Condenser water pump (headered); Type: End suction, VSD; Flow: 1,000 USgpm; Head: 80 ft; Motor: 30 kW, 380/3/50; Slot: CDP02
CT-01/1 | ct | 4000 | 6000 | 35900 | 0 | 2600 | 2600 | 2700 | CT01_01 | Type: Crossflow, induced draft (FRP); Cell: 1 of 2; Capacity: 420 TR per tower; Fan: 5.5 kW VSD; Slot: CT01
CT-01/2 | ct | 6800 | 6000 | 35900 | 0 | 2600 | 2600 | 2700 | CT01_02 | Type: Crossflow, induced draft (FRP); Cell: 2 of 2; Capacity: 420 TR per tower; Fan: 5.5 kW VSD; Slot: CT01
CT-02/1 | ct | 9600 | 6000 | 35900 | 0 | 2600 | 2600 | 2700 | CT02_01 | Type: Crossflow, induced draft (FRP); Cell: 1 of 2; Capacity: 420 TR per tower; Fan: 5.5 kW VSD; Slot: CT02
CT-02/2 | ct | 12400 | 6000 | 35900 | 0 | 2600 | 2600 | 2700 | CT02_02 | Type: Crossflow, induced draft (FRP); Cell: 2 of 2; Capacity: 420 TR per tower; Fan: 5.5 kW VSD; Slot: CT02
ET-01 | exptank | 31000 | 12900 | 0 | 0 | 900 | 900 | 1600 |  | Service: Expansion tank; Volume: 1,000 L
DPB-01 | bypass | 30000 | 8600 | 0 | 0 | 2400 | 500 | 800 | Byp | Service: CHW minimum-flow bypass
CP-01 | panel | 2500 | 14600 | 0 | 0 | 2400 | 500 | 2100 | Plant | Service: CPMS control panel (Niagara JACE / Supervisor); Station: ALT_CP_Ref_V7_9
AHU-01 | ahu | 50000 | 12500 | 0 | 0 | 3600 | 1800 | 2100 | AHU01 | Type: Air handling unit, CHW coil, VSD fan; Airflow: 12,000 CFM; Serves: Lobby / reception / open office
AHU-02 | ahu | 58000 | 12500 | 0 | 0 | 3600 | 1800 | 2100 | AHU02 | Type: Air handling unit, CHW coil, VSD fan; Airflow: 12,000 CFM; Serves: Meeting / training / executive
OAU-01 | ahu | 50000 | 33000 | 34900 | 0 | 4200 | 2000 | 2200 | OAU01 | Type: Outdoor air unit (dew point control)
FCU-01 | fcu | 4000 | 36500 | 4600 | 0 | 1400 | 700 | 300 | FCU01 | Type: Fan coil unit, 3-speed fan, on/off valve
FCU-02 | fcu | 15000 | 36500 | 4600 | 0 | 1400 | 700 | 300 | FCU02 | Type: Fan coil unit, 3-speed fan, on/off valve
FCU-03 | fcu | 26000 | 36500 | 4600 | 0 | 1400 | 700 | 300 | FCU03 | Type: Fan coil unit, 3-speed fan, on/off valve
FCU-04 | fcu | 37000 | 36500 | 4600 | 0 | 1400 | 700 | 300 | FCU04 | Type: Fan coil unit, 3-speed fan, on/off valve
AHU-F02 | ahu | 35000 | 17500 | 5500 | 0 | 3600 | 1800 | 2100 | AHU_F02 | Type: Air handling unit, CHW coil, VSD fan; Airflow: 12,000 CFM; Serves: Floor 2 (4 zones)
AHU-F03 | ahu | 35000 | 17500 | 9700 | 0 | 3600 | 1800 | 2100 | AHU_F03 | Type: Air handling unit, CHW coil, VSD fan; Airflow: 12,000 CFM; Serves: Floor 3 (4 zones)
AHU-F04 | ahu | 35000 | 17500 | 13900 | 0 | 3600 | 1800 | 2100 | AHU_F04 | Type: Air handling unit, CHW coil, VSD fan; Airflow: 12,000 CFM; Serves: Floor 4 (4 zones)
AHU-F05 | ahu | 35000 | 17500 | 18100 | 0 | 3600 | 1800 | 2100 | AHU_F05 | Type: Air handling unit, CHW coil, VSD fan; Airflow: 12,000 CFM; Serves: Floor 5 (4 zones)
AHU-F06 | ahu | 35000 | 17500 | 22300 | 0 | 3600 | 1800 | 2100 | AHU_F06 | Type: Air handling unit, CHW coil, VSD fan; Airflow: 12,000 CFM; Serves: Floor 6 (4 zones)
AHU-F07 | ahu | 35000 | 17500 | 26500 | 0 | 3600 | 1800 | 2100 | AHU_F07 | Type: Air handling unit, CHW coil, VSD fan; Airflow: 12,000 CFM; Serves: Floor 7 (4 zones)
AHU-F08 | ahu | 35000 | 17500 | 30700 | 0 | 3600 | 1800 | 2100 | AHU_F08 | Type: Air handling unit, CHW coil, VSD fan; Airflow: 12,000 CFM; Serves: Floor 8 (4 zones)
EF-01 | fan | 20000 | 30000 | 34900 | 0 | 1200 | 1200 | 1100 | EF01 | Type: Fan
EF-02 | fan | 26000 | 30000 | 34900 | 0 | 1200 | 1200 | 1100 | EF02 | Type: Fan
EF-03 | fan | 42000 | 4000 | 3800 | 0 | 1200 | 1200 | 1100 | EF03 | Type: Fan
CPEF-01 | fan | 58000 | 30000 | 34900 | 0 | 1200 | 1200 | 1100 | CPEF01 | Type: Fan
LSF-01 | fan | 44000 | 24000 | 34900 | 0 | 1200 | 1200 | 1100 | LSF01 | Type: Fan
SEF-01 | fan | 46000 | 18000 | 34900 | 0 | 1200 | 1200 | 1100 | SEF01 | Type: Fan

## COBie_Component
Name | CreatedBy | CreatedOn | TypeName | Space | Description | ExtSystem | ExtObject | SerialNumber | InstallationDate | TagNumber | BarCode | AssetIdentifier
CH-01 | AETERLINK BIM generator | 2026-10-08 | Water-cooled screw / centrifugal (reference) | Chiller room |  | model.py | chiller | n/a | n/a | CH-01 | n/a | CH01
CH-02 | AETERLINK BIM generator | 2026-10-08 | Water-cooled screw / centrifugal (reference) | Chiller room |  | model.py | chiller | n/a | n/a | CH-02 | n/a | CH02
CHP-01 | AETERLINK BIM generator | 2026-10-08 | Chilled water pump (primary-variable, headered) | Chiller room | Chilled water pump (primary-variable, headered) | model.py | pump | n/a | n/a | CHP-01 | n/a | CHP01
CHP-02 | AETERLINK BIM generator | 2026-10-08 | Chilled water pump (primary-variable, headered) | Chiller room | Chilled water pump (primary-variable, headered) | model.py | pump | n/a | n/a | CHP-02 | n/a | CHP02
CDP-01 | AETERLINK BIM generator | 2026-10-08 | Condenser water pump (headered) | Chiller room | Condenser water pump (headered) | model.py | pump | n/a | n/a | CDP-01 | n/a | CDP01
CDP-02 | AETERLINK BIM generator | 2026-10-08 | Condenser water pump (headered) | Chiller room | Condenser water pump (headered) | model.py | pump | n/a | n/a | CDP-02 | n/a | CDP02
CT-01/1 | AETERLINK BIM generator | 2026-10-08 | Cooling tower cell, Crossflow, induced draft (FRP) | Roof | Crossflow, induced draft (FRP) | model.py | ct | n/a | n/a | CT-01/1 | n/a | CT01_01
CT-01/2 | AETERLINK BIM generator | 2026-10-08 | Cooling tower cell, Crossflow, induced draft (FRP) | Roof | Crossflow, induced draft (FRP) | model.py | ct | n/a | n/a | CT-01/2 | n/a | CT01_02
CT-02/1 | AETERLINK BIM generator | 2026-10-08 | Cooling tower cell, Crossflow, induced draft (FRP) | Roof | Crossflow, induced draft (FRP) | model.py | ct | n/a | n/a | CT-02/1 | n/a | CT02_01
CT-02/2 | AETERLINK BIM generator | 2026-10-08 | Cooling tower cell, Crossflow, induced draft (FRP) | Roof | Crossflow, induced draft (FRP) | model.py | ct | n/a | n/a | CT-02/2 | n/a | CT02_02
ET-01 | AETERLINK BIM generator | 2026-10-08 | Expansion tank | Chiller room | Expansion tank | model.py | exptank | n/a | n/a | ET-01 | n/a | n/a
DPB-01 | AETERLINK BIM generator | 2026-10-08 | CHW minimum-flow bypass | Chiller room | CHW minimum-flow bypass | model.py | bypass | n/a | n/a | DPB-01 | n/a | Byp
CP-01 | AETERLINK BIM generator | 2026-10-08 | CPMS control panel (Niagara JACE / Supervisor) | Chiller room | CPMS control panel (Niagara JACE / Supervisor) | model.py | panel | n/a | n/a | CP-01 | n/a | Plant
AHU-01 | AETERLINK BIM generator | 2026-10-08 | Cooling tower cell, Air handling unit, CHW coil, VSD fan | Chiller room | Air handling unit, CHW coil, VSD fan | model.py | ahu | n/a | n/a | AHU-01 | n/a | AHU01
AHU-02 | AETERLINK BIM generator | 2026-10-08 | Cooling tower cell, Air handling unit, CHW coil, VSD fan | Chiller room | Air handling unit, CHW coil, VSD fan | model.py | ahu | n/a | n/a | AHU-02 | n/a | AHU02
OAU-01 | AETERLINK BIM generator | 2026-10-08 | Cooling tower cell, Outdoor air unit (dew point control) | Chiller room | Outdoor air unit (dew point control) | model.py | ahu | n/a | n/a | OAU-01 | n/a | OAU01
FCU-01 | AETERLINK BIM generator | 2026-10-08 | Cooling tower cell, Fan coil unit, 3-speed fan, on/off valve | Chiller room | Fan coil unit, 3-speed fan, on/off valve | model.py | fcu | n/a | n/a | FCU-01 | n/a | FCU01
FCU-02 | AETERLINK BIM generator | 2026-10-08 | Cooling tower cell, Fan coil unit, 3-speed fan, on/off valve | Chiller room | Fan coil unit, 3-speed fan, on/off valve | model.py | fcu | n/a | n/a | FCU-02 | n/a | FCU02
FCU-03 | AETERLINK BIM generator | 2026-10-08 | Cooling tower cell, Fan coil unit, 3-speed fan, on/off valve | Chiller room | Fan coil unit, 3-speed fan, on/off valve | model.py | fcu | n/a | n/a | FCU-03 | n/a | FCU03
FCU-04 | AETERLINK BIM generator | 2026-10-08 | Cooling tower cell, Fan coil unit, 3-speed fan, on/off valve | Chiller room | Fan coil unit, 3-speed fan, on/off valve | model.py | fcu | n/a | n/a | FCU-04 | n/a | FCU04
AHU-F02 | AETERLINK BIM generator | 2026-10-08 | Cooling tower cell, Air handling unit, CHW coil, VSD fan | Chiller room | Air handling unit, CHW coil, VSD fan | model.py | ahu | n/a | n/a | AHU-F02 | n/a | AHU_F02
AHU-F03 | AETERLINK BIM generator | 2026-10-08 | Cooling tower cell, Air handling unit, CHW coil, VSD fan | Chiller room | Air handling unit, CHW coil, VSD fan | model.py | ahu | n/a | n/a | AHU-F03 | n/a | AHU_F03
AHU-F04 | AETERLINK BIM generator | 2026-10-08 | Cooling tower cell, Air handling unit, CHW coil, VSD fan | Chiller room | Air handling unit, CHW coil, VSD fan | model.py | ahu | n/a | n/a | AHU-F04 | n/a | AHU_F04
AHU-F05 | AETERLINK BIM generator | 2026-10-08 | Cooling tower cell, Air handling unit, CHW coil, VSD fan | Chiller room | Air handling unit, CHW coil, VSD fan | model.py | ahu | n/a | n/a | AHU-F05 | n/a | AHU_F05
AHU-F06 | AETERLINK BIM generator | 2026-10-08 | Cooling tower cell, Air handling unit, CHW coil, VSD fan | Chiller room | Air handling unit, CHW coil, VSD fan | model.py | ahu | n/a | n/a | AHU-F06 | n/a | AHU_F06
AHU-F07 | AETERLINK BIM generator | 2026-10-08 | Cooling tower cell, Air handling unit, CHW coil, VSD fan | Chiller room | Air handling unit, CHW coil, VSD fan | model.py | ahu | n/a | n/a | AHU-F07 | n/a | AHU_F07
AHU-F08 | AETERLINK BIM generator | 2026-10-08 | Cooling tower cell, Air handling unit, CHW coil, VSD fan | Chiller room | Air handling unit, CHW coil, VSD fan | model.py | ahu | n/a | n/a | AHU-F08 | n/a | AHU_F08
EF-01 | AETERLINK BIM generator | 2026-10-08 | Cooling tower cell, Fan | Chiller room | Fan | model.py | fan | n/a | n/a | EF-01 | n/a | EF01
EF-02 | AETERLINK BIM generator | 2026-10-08 | Cooling tower cell, Fan | Chiller room | Fan | model.py | fan | n/a | n/a | EF-02 | n/a | EF02
EF-03 | AETERLINK BIM generator | 2026-10-08 | Cooling tower cell, Fan | Chiller room | Fan | model.py | fan | n/a | n/a | EF-03 | n/a | EF03
CPEF-01 | AETERLINK BIM generator | 2026-10-08 | Cooling tower cell, Fan | Chiller room | Fan | model.py | fan | n/a | n/a | CPEF-01 | n/a | CPEF01
LSF-01 | AETERLINK BIM generator | 2026-10-08 | Cooling tower cell, Fan | Chiller room | Fan | model.py | fan | n/a | n/a | LSF-01 | n/a | LSF01
SEF-01 | AETERLINK BIM generator | 2026-10-08 | Cooling tower cell, Fan | Chiller room | Fan | model.py | fan | n/a | n/a | SEF-01 | n/a | SEF01
MBFV-001 | AETERLINK BIM generator | 2026-10-08 | Motorized butterfly valve (on/off, 24 Vac) | Chiller room | MBFV on CHR-P1 | model.py | valve | n/a | n/a | CHP01 suction | n/a | Gfx_CHP01_SuctionMV_Pos
STRAINER-002 | AETERLINK BIM generator | 2026-10-08 | Y-strainer, 20 mesh | Chiller room | STRAINER on CHR-P1 | model.py | valve | n/a | n/a | STRAINER-002 | n/a | n/a
CHECK-005 | AETERLINK BIM generator | 2026-10-08 | Check valve, silent / dual plate | Chiller room | CHECK on CHR-D1 | model.py | valve | n/a | n/a | CHECK-005 | n/a | n/a
MBFV-006 | AETERLINK BIM generator | 2026-10-08 | Motorized butterfly valve (on/off, 24 Vac) | Chiller room | MBFV on CHR-D1 | model.py | valve | n/a | n/a | CHP01 discharge MV | n/a | Gfx_CHP01_DischargeMV_Pos
MBFV-007 | AETERLINK BIM generator | 2026-10-08 | Motorized butterfly valve (on/off, 24 Vac) | Chiller room | MBFV on CHR-P2 | model.py | valve | n/a | n/a | CHP02 suction | n/a | Gfx_CHP02_SuctionMV_Pos
STRAINER-008 | AETERLINK BIM generator | 2026-10-08 | Y-strainer, 20 mesh | Chiller room | STRAINER on CHR-P2 | model.py | valve | n/a | n/a | STRAINER-008 | n/a | n/a
CHECK-011 | AETERLINK BIM generator | 2026-10-08 | Check valve, silent / dual plate | Chiller room | CHECK on CHR-D2 | model.py | valve | n/a | n/a | CHECK-011 | n/a | n/a
MBFV-012 | AETERLINK BIM generator | 2026-10-08 | Motorized butterfly valve (on/off, 24 Vac) | Chiller room | MBFV on CHR-D2 | model.py | valve | n/a | n/a | CHP02 discharge MV | n/a | Gfx_CHP02_DischargeMV_Pos
MBFV-013 | AETERLINK BIM generator | 2026-10-08 | Motorized butterfly valve (on/off, 24 Vac) | Chiller room | MBFV on CDS-P1 | model.py | valve | n/a | n/a | CDP01 suction | n/a | Gfx_CDP01_SuctionMV_Pos
STRAINER-014 | AETERLINK BIM generator | 2026-10-08 | Y-strainer, 20 mesh | Chiller room | STRAINER on CDS-P1 | model.py | valve | n/a | n/a | STRAINER-014 | n/a | n/a
CHECK-017 | AETERLINK BIM generator | 2026-10-08 | Check valve, silent / dual plate | Chiller room | CHECK on CDS-D1 | model.py | valve | n/a | n/a | CHECK-017 | n/a | n/a
MBFV-018 | AETERLINK BIM generator | 2026-10-08 | Motorized butterfly valve (on/off, 24 Vac) | Chiller room | MBFV on CDS-D1 | model.py | valve | n/a | n/a | CDP01 discharge MV | n/a | Gfx_CDP01_DischargeMV_Pos
MBFV-019 | AETERLINK BIM generator | 2026-10-08 | Motorized butterfly valve (on/off, 24 Vac) | Chiller room | MBFV on CDS-P2 | model.py | valve | n/a | n/a | CDP02 suction | n/a | Gfx_CDP02_SuctionMV_Pos
STRAINER-020 | AETERLINK BIM generator | 2026-10-08 | Y-strainer, 20 mesh | Chiller room | STRAINER on CDS-P2 | model.py | valve | n/a | n/a | STRAINER-020 | n/a | n/a
CHECK-023 | AETERLINK BIM generator | 2026-10-08 | Check valve, silent / dual plate | Chiller room | CHECK on CDS-D2 | model.py | valve | n/a | n/a | CHECK-023 | n/a | n/a
MBFV-024 | AETERLINK BIM generator | 2026-10-08 | Motorized butterfly valve (on/off, 24 Vac) | Chiller room | MBFV on CDS-D2 | model.py | valve | n/a | n/a | CDP02 discharge MV | n/a | Gfx_CDP02_DischargeMV_Pos
BFV-025 | AETERLINK BIM generator | 2026-10-08 | Butterfly valve, lug type, PN16 | Chiller room | BFV on CHR-E1 | model.py | valve | n/a | n/a | BFV-025 | n/a | n/a
MBFV-026 | AETERLINK BIM generator | 2026-10-08 | Motorized butterfly valve (on/off, 24 Vac) | Chiller room | MBFV on CHR-E1 | model.py | valve | n/a | n/a | CH01 CHW isolation | n/a | Gfx_CH01_ChwIso_Pos
FS-030 | AETERLINK BIM generator | 2026-10-08 | Paddle flow switch | Chiller room | FS on CHS-E1 | model.py | valve | n/a | n/a | CH01 evaporator flow switch | n/a | n/a
MCV-031 | AETERLINK BIM generator | 2026-10-08 | Motorized control valve (modulating 0-10 V, position feedback) | Chiller room | MCV on CHS-E1 | model.py | valve | n/a | n/a | CH01 CHW flow control | n/a | Gfx_CH01_ChwFCV_Pos
BFV-032 | AETERLINK BIM generator | 2026-10-08 | Butterfly valve, lug type, PN16 | Chiller room | BFV on CDS-C1 | model.py | valve | n/a | n/a | BFV-032 | n/a | n/a
MBFV-033 | AETERLINK BIM generator | 2026-10-08 | Motorized butterfly valve (on/off, 24 Vac) | Chiller room | MBFV on CDS-C1 | model.py | valve | n/a | n/a | CH01 CDW isolation | n/a | Gfx_CH01_CdwIso_Pos
FS-036 | AETERLINK BIM generator | 2026-10-08 | Paddle flow switch | Chiller room | FS on CDR-C1 | model.py | valve | n/a | n/a | CH01 condenser flow switch | n/a | n/a
MCV-037 | AETERLINK BIM generator | 2026-10-08 | Motorized control valve (modulating 0-10 V, position feedback) | Chiller room | MCV on CDR-C1 | model.py | valve | n/a | n/a | CH01 head-pressure valve | n/a | Gfx_CH01_CdwHPV_Pos
BFV-038 | AETERLINK BIM generator | 2026-10-08 | Butterfly valve, lug type, PN16 | Chiller room | BFV on CHR-E2 | model.py | valve | n/a | n/a | BFV-038 | n/a | n/a
MBFV-039 | AETERLINK BIM generator | 2026-10-08 | Motorized butterfly valve (on/off, 24 Vac) | Chiller room | MBFV on CHR-E2 | model.py | valve | n/a | n/a | CH02 CHW isolation | n/a | Gfx_CH02_ChwIso_Pos
FS-043 | AETERLINK BIM generator | 2026-10-08 | Paddle flow switch | Chiller room | FS on CHS-E2 | model.py | valve | n/a | n/a | CH02 evaporator flow switch | n/a | n/a
MCV-044 | AETERLINK BIM generator | 2026-10-08 | Motorized control valve (modulating 0-10 V, position feedback) | Chiller room | MCV on CHS-E2 | model.py | valve | n/a | n/a | CH02 CHW flow control | n/a | Gfx_CH02_ChwFCV_Pos
BFV-045 | AETERLINK BIM generator | 2026-10-08 | Butterfly valve, lug type, PN16 | Chiller room | BFV on CDS-C2 | model.py | valve | n/a | n/a | BFV-045 | n/a | n/a
MBFV-046 | AETERLINK BIM generator | 2026-10-08 | Motorized butterfly valve (on/off, 24 Vac) | Chiller room | MBFV on CDS-C2 | model.py | valve | n/a | n/a | CH02 CDW isolation | n/a | Gfx_CH02_CdwIso_Pos
FS-049 | AETERLINK BIM generator | 2026-10-08 | Paddle flow switch | Chiller room | FS on CDR-C2 | model.py | valve | n/a | n/a | CH02 condenser flow switch | n/a | n/a
MCV-050 | AETERLINK BIM generator | 2026-10-08 | Motorized control valve (modulating 0-10 V, position feedback) | Chiller room | MCV on CDR-C2 | model.py | valve | n/a | n/a | CH02 head-pressure valve | n/a | Gfx_CH02_CdwHPV_Pos
BFV-051 | AETERLINK BIM generator | 2026-10-08 | Butterfly valve, lug type, PN16 | Roof | BFV on CDR-T1 | model.py | valve | n/a | n/a | BFV-051 | n/a | n/a
MBFV-052 | AETERLINK BIM generator | 2026-10-08 | Motorized butterfly valve (on/off, 24 Vac) | Roof | MBFV on CDR-T1 | model.py | valve | n/a | n/a | CT01 inlet | n/a | Gfx_CT01_InletMV_Pos
MBFV-053 | AETERLINK BIM generator | 2026-10-08 | Motorized butterfly valve (on/off, 24 Vac) | Roof | MBFV on CDS-T1 | model.py | valve | n/a | n/a | CT01 outlet | n/a | Gfx_CT01_OutletMV_Pos
BFV-054 | AETERLINK BIM generator | 2026-10-08 | Butterfly valve, lug type, PN16 | Roof | BFV on CDS-T1 | model.py | valve | n/a | n/a | BFV-054 | n/a | n/a
BFV-055 | AETERLINK BIM generator | 2026-10-08 | Butterfly valve, lug type, PN16 | Roof | BFV on CDR-T2 | model.py | valve | n/a | n/a | BFV-055 | n/a | n/a
MBFV-056 | AETERLINK BIM generator | 2026-10-08 | Motorized butterfly valve (on/off, 24 Vac) | Roof | MBFV on CDR-T2 | model.py | valve | n/a | n/a | CT01 inlet | n/a | Gfx_CT01_InletMV_Pos
MBFV-057 | AETERLINK BIM generator | 2026-10-08 | Motorized butterfly valve (on/off, 24 Vac) | Roof | MBFV on CDS-T2 | model.py | valve | n/a | n/a | CT01 outlet | n/a | Gfx_CT01_OutletMV_Pos
BFV-058 | AETERLINK BIM generator | 2026-10-08 | Butterfly valve, lug type, PN16 | Roof | BFV on CDS-T2 | model.py | valve | n/a | n/a | BFV-058 | n/a | n/a
BFV-059 | AETERLINK BIM generator | 2026-10-08 | Butterfly valve, lug type, PN16 | Roof | BFV on CDR-T3 | model.py | valve | n/a | n/a | BFV-059 | n/a | n/a
MBFV-060 | AETERLINK BIM generator | 2026-10-08 | Motorized butterfly valve (on/off, 24 Vac) | Roof | MBFV on CDR-T3 | model.py | valve | n/a | n/a | CT02 inlet | n/a | Gfx_CT02_InletMV_Pos
MBFV-061 | AETERLINK BIM generator | 2026-10-08 | Motorized butterfly valve (on/off, 24 Vac) | Roof | MBFV on CDS-T3 | model.py | valve | n/a | n/a | CT02 outlet | n/a | Gfx_CT02_OutletMV_Pos
BFV-062 | AETERLINK BIM generator | 2026-10-08 | Butterfly valve, lug type, PN16 | Roof | BFV on CDS-T3 | model.py | valve | n/a | n/a | BFV-062 | n/a | n/a
BFV-063 | AETERLINK BIM generator | 2026-10-08 | Butterfly valve, lug type, PN16 | Roof | BFV on CDR-T4 | model.py | valve | n/a | n/a | BFV-063 | n/a | n/a
MBFV-064 | AETERLINK BIM generator | 2026-10-08 | Motorized butterfly valve (on/off, 24 Vac) | Roof | MBFV on CDR-T4 | model.py | valve | n/a | n/a | CT02 inlet | n/a | Gfx_CT02_InletMV_Pos
MBFV-065 | AETERLINK BIM generator | 2026-10-08 | Motorized butterfly valve (on/off, 24 Vac) | Roof | MBFV on CDS-T4 | model.py | valve | n/a | n/a | CT02 outlet | n/a | Gfx_CT02_OutletMV_Pos
BFV-066 | AETERLINK BIM generator | 2026-10-08 | Butterfly valve, lug type, PN16 | Roof | BFV on CDS-T4 | model.py | valve | n/a | n/a | BFV-066 | n/a | n/a
MCV-067 | AETERLINK BIM generator | 2026-10-08 | Motorized control valve (modulating 0-10 V, position feedback) | Chiller room | MCV on CHS-F2 | model.py | valve | n/a | n/a | AHU_F02 CHW valve | n/a | AHU_F02_ValveCmd
BFV-068 | AETERLINK BIM generator | 2026-10-08 | Butterfly valve, lug type, PN16 | Chiller room | BFV on CHR-F2 | model.py | valve | n/a | n/a | BFV-068 | n/a | n/a
MCV-069 | AETERLINK BIM generator | 2026-10-08 | Motorized control valve (modulating 0-10 V, position feedback) | Chiller room | MCV on CHS-F3 | model.py | valve | n/a | n/a | AHU_F03 CHW valve | n/a | AHU_F03_ValveCmd
BFV-070 | AETERLINK BIM generator | 2026-10-08 | Butterfly valve, lug type, PN16 | Chiller room | BFV on CHR-F3 | model.py | valve | n/a | n/a | BFV-070 | n/a | n/a
MCV-071 | AETERLINK BIM generator | 2026-10-08 | Motorized control valve (modulating 0-10 V, position feedback) | Chiller room | MCV on CHS-F4 | model.py | valve | n/a | n/a | AHU_F04 CHW valve | n/a | AHU_F04_ValveCmd
BFV-072 | AETERLINK BIM generator | 2026-10-08 | Butterfly valve, lug type, PN16 | Chiller room | BFV on CHR-F4 | model.py | valve | n/a | n/a | BFV-072 | n/a | n/a
MCV-073 | AETERLINK BIM generator | 2026-10-08 | Motorized control valve (modulating 0-10 V, position feedback) | Chiller room | MCV on CHS-F5 | model.py | valve | n/a | n/a | AHU_F05 CHW valve | n/a | AHU_F05_ValveCmd
BFV-074 | AETERLINK BIM generator | 2026-10-08 | Butterfly valve, lug type, PN16 | Chiller room | BFV on CHR-F5 | model.py | valve | n/a | n/a | BFV-074 | n/a | n/a
MCV-075 | AETERLINK BIM generator | 2026-10-08 | Motorized control valve (modulating 0-10 V, position feedback) | Chiller room | MCV on CHS-F6 | model.py | valve | n/a | n/a | AHU_F06 CHW valve | n/a | AHU_F06_ValveCmd
BFV-076 | AETERLINK BIM generator | 2026-10-08 | Butterfly valve, lug type, PN16 | Chiller room | BFV on CHR-F6 | model.py | valve | n/a | n/a | BFV-076 | n/a | n/a
MCV-077 | AETERLINK BIM generator | 2026-10-08 | Motorized control valve (modulating 0-10 V, position feedback) | Chiller room | MCV on CHS-F7 | model.py | valve | n/a | n/a | AHU_F07 CHW valve | n/a | AHU_F07_ValveCmd
BFV-078 | AETERLINK BIM generator | 2026-10-08 | Butterfly valve, lug type, PN16 | Chiller room | BFV on CHR-F7 | model.py | valve | n/a | n/a | BFV-078 | n/a | n/a
MCV-079 | AETERLINK BIM generator | 2026-10-08 | Motorized control valve (modulating 0-10 V, position feedback) | Chiller room | MCV on CHS-F8 | model.py | valve | n/a | n/a | AHU_F08 CHW valve | n/a | AHU_F08_ValveCmd
BFV-080 | AETERLINK BIM generator | 2026-10-08 | Butterfly valve, lug type, PN16 | Chiller room | BFV on CHR-F8 | model.py | valve | n/a | n/a | BFV-080 | n/a | n/a
FM-082 | AETERLINK BIM generator | 2026-10-08 | Electromagnetic flow meter | Chiller room | FM on CHS-H | model.py | valve | n/a | n/a | CHWFlow | n/a | CHWFlow
PT-083 | AETERLINK BIM generator | 2026-10-08 | Differential pressure transmitter 0-4 bar | Chiller room | PT on CHS-R | model.py | valve | n/a | n/a | CHWDP | n/a | n/a
BFV-086 | AETERLINK BIM generator | 2026-10-08 | Butterfly valve, lug type, PN16 | Chiller room | BFV on CHW-BP | model.py | valve | n/a | n/a | BFV-086 | n/a | n/a
MCV-087 | AETERLINK BIM generator | 2026-10-08 | Motorized control valve (modulating 0-10 V, position feedback) | Chiller room | MCV on CHW-BP | model.py | valve | n/a | n/a | CHW bypass valve | n/a | Gfx_CHW_BypassMV_Pos
BFV-088 | AETERLINK BIM generator | 2026-10-08 | Butterfly valve, lug type, PN16 | Chiller room | BFV on CHW-BP | model.py | valve | n/a | n/a | BFV-088 | n/a | n/a
BFV-089 | AETERLINK BIM generator | 2026-10-08 | Butterfly valve, lug type, PN16 | Chiller room | BFV on CHW-ET | model.py | valve | n/a | n/a | BFV-089 | n/a | n/a
FM-091 | AETERLINK BIM generator | 2026-10-08 | Electromagnetic flow meter | Chiller room | FM on CDS-CH | model.py | valve | n/a | n/a | CDW_Flow | n/a | CDW_Flow